## Input
Category | Parameter | Permissible_Values | Unit | Selected_Value
| WF Position |  |  | pipe
Working Fluid Features | Mass Flow | - | kg/s | 2
| P_in | - | Pa | 1000000
| T_in | - | K | 403
| T_out |  |  | 393
| Q_in | - |  | None
| Q_out |  |  | None
| P_loss | - | Pa | 10000
Secondary Fluid Features | P_in | - | Pa | 101325
| T_in | - | K | None
| T_out |  |  | None
| Q_in | - |  | 0.2
| Q_out |  |  | 0.3
| P_loss | - | Pa | 10000
| Uo Overall Heat Transfer Coefficient (First Guess) | https://www.engineersedge.com/thermodynamics/overall_heat_transfer-table.htm | W/(m2.K) | 300
| max h fouling (tube-side) | - | W/(m2.K) | 10000
| max h fouling (shell-side) | - | W/(m2.K) | 10000
| Mechanical Oversizing Factor |  |  | 5
| Mechanical Safety Factor |  |  | 1.1
| TEMA Category | E - F -…. |  | E
| Bundle Type |  |  | 2
| Rear Head Type |  |  | U
| n° passages tubes |  |  | 4
| Tubes Nominal Diameter |  | inch | 0.25
| n° passages shell |  |  | 1
| Tubes Disposition |  |  | t
| Pitch Ratio |  |  | 1.25
| Exchanger Lenght |  | m | 2
| Baffle Spacing |  |  | 0.2
| Baffle Cut |  |  | 20
| Corrosion allowances |  | m | 0.0005
| Tube Surface roughness |  | m | 1e-06

## Foglio1
Variables | 1 | 2 | 3 | 4 | 5 | 1 | 2
Uo | 300 | 600 | 900 | 1200 | 1500 | 300 | 300
Uo_star | 191 | 230 | 230 | 230 | 320 | 235 | 305
Q [W] | 83942 | 83942 | 83942 | 83942 | 83942 | 83942 | 83942
Q_star | 96728 | 75289 | 75289 | 75289 | 57558 | 154943 | 144745
L [m] | 2 | 2 | 2 | 2 | 2 | 2 | 2
np_tube | 2 | 2 | 2 | 2 | 2 | 4 | 4
nt | 186 | 120 | 120 | 120 | 66 | 242 | 174
D_shell_int | 0.25745 | 0.20637 | 0.20637 | 0.20637 | 0.16827 | 0.30323 | 0.25745
D_shell_ext | 0.27305 | 0.21907 | 0.21907 | 0.21907 | 0.15405 | 0.32385 | 0.27305
Re_mean_tube | 3713 | 5755 | 5755 | 5755 | 19464 | 5707 | 7938
Re_mean_shell | 4169 | 6488 | 6488 | 6488 | 11644 | 3005 | 4169
D_eq_tube | 0.0052 | 0.0052 | 0.0052 | 0.0052 | 0.0052 | 0.0026 | 0.0026
D_eq_shell | 0.0097 | 0.0097 | 0.0097 | 0.0097 | 0.0097 | 0.0097 | 0.0097
alfa_tube | 420 | 477 | 477 | 477 | 702 | 951 | 1126
alfa_shell | 570 | 811 | 811 | 811 | 1113 | 397 | 570
Delta_P_tube | 157 | 367 | 367 | 367 | 1077 | 686 | 1236
Delta_P_shell | 3610 | 8132 | 8132 | 8132 | 23796 | 1217 | 3610